## Check list (twice per day):

Scope of the work:

Detectors for the OT are stored in barrack 6791. They are flushed with CO2 and heated 	to a temperature of ~40°C. During the Christmas break it has to be guaranteed that the 	gas flow is present during that time and that the temperature is at the desired level.

It must be avoided in any case that the modules cool down to a temperature below 10°C.

Hazards:

In barrack 6791 detector modules are flushed continuously with CO2. In case of a leak inside the barrack the oxygen level may be reduced. Risk of asphyxiation!

Precautions:

- Before you enter point 8 call pompiers on 74848. Explain reason and duration for stay at point 8.

- Before you enter barrack 6791 check value on CO2 meter to be below 1,5%. If the value exceeds 1,5% do not enter! Call Sebastian Bachmann (162038) or Antonio Pellegrino (162572).

- Whenever you stay inside barrack 6791 keep the door open to ensure good circulation of air.

- After you finish work call 74444 to check out.

Keys:

- Keys of the barrack 6791 and of the main building are fixed to the bottom of the barrack as indicated in the picture.

Contacts:

- Sebastian Bachmann 162038

- Antonio Pellegrino 162572

- Bernard Corajod 163350

- Binbin Cheng 162196

- Anatoli Kashchuk 162988

- Burkhard Schmidt 162985

Check list:

- Check power in barrack 6791.

- Check that all 3 radiators are on.

- Check gas flow on bubbler.

- Check PC is on, in case PC is shut down switch it on and login as

User: OT

Password: OT2007

(use capitals!)

- Fill log book:

-    Date + Time

  - Actual temperature sensor IN

  - Actual temperature sensor OUT

  - Tmin and Tmax on sensor IN and sensor OUT

  - Actual Humidity sensor IN

  - Actual Humidity sensor OUT

  - Gas flow on Rotameter

  - Pressure on pressure meter

## Emergency cases:

- Gas flow stopped:

  - Try to recuperate gas flow.

  - If not possible: Lower radiator 2 + 3 to level 1, setting 3.

Lower radiator 4 to setting 4.

Temperature should stabilize around 20°C – 25°C.

Call Antonio Pellegrino 162572; Sebastian Bachmann 162038.

- Temperature below 35°C

  - Increase radiator settings moderately.

  - Temperature should stabilize at about 35°C - 40°C.

- Temperature above 45°C:

  - Lower radiator settings.

  - Temperature should stabilize at about 40°C.

- Power cut:

  - Check fuses in EBD 105/8F.

  - In case of a blown fuse: Switch on fuse.

  - When fuses are settled:

Check power in barrack.

Check that radiators switch on.

  - If this does not help: Call TI, 72231, 72201

Call Antonio Pellegrino 162572; Sebastian Bachmann 162038

  - If TI recuperates power:

Check power in barrack 6791 is back.

Check radiators are functional.

If TI cannot recuperate power within 1 day:

Call Antonio Pellegrino 162572; Sebastian Bachmann 162038

Call Bernard Corajod: 163350

- Switch off gas flow.

- Disconnect boxes from gas.

- Organize together with Bernard to bring modules into building 2885.

# Text boxes

Rotameter

Pressure meter

Bubbler

Thermometer

Position of keys for barrack 6791 and main building 2885 (SX8)

CO2 meter